## Sheet1
Basic PV Voltage Drop Calculator
| Wire Temp | [6 empty] | Voltage
| (c ) or ( f ) | Fahrenheit | Celsius |  |  |  |  | Array Voltage | Battery Bank Voltage
| f | 70 | 21.1111 |  |  |  |  | 60 | 48
|  |  | Total | Resistance | Array
| Item Name | AWG | Feet | Ohms | Panel (Volts) | Panel (Amps) | Voltage drop | Voltage drop %
String 1 | Panel 1 | 10 | 10 | 0.010033 | 60 | 6.62 | 0.066416 | 0.1107%
String 2 | Panel 2 | 10 | 10 | 0.010033 | 60 | 6.62 | 0.066416 | 0.1107%
String 2 | Panel 3 | 10 | 8 | 0 | 60 | 0 | 0 | 0%
String 2 | Panel 4 | 10 | 8 | 0 | 60 | 0 | 0 | 0%
String 2 | Panel 5 | 10 | 8 | 0 | 60 | 0 | 0 | 0%
String 2 | Panel 6 | 10 | 8 | 0 | 60 | 0 | 0 | 0%
String 2 | Panel 7 | 10 | 8 | 0 | 60 | 0 | 0 | 0%
String 3 | Panel 8 | 10 | 8 | 0 | 60 | 0 | 0 | 0%
| Array To Combiner Box |  | 0.010033 | 0.0050163 | 60 | 13.24 | 0.066416 | 0.1107%
| Combiner box to Breaker | 4 | 40 | 0.0099834 | 60 | 13.24 | 0.13218 | 0.2203%
| Breaker box to Controller | 6 | 2 | 0.00079365 | 60 | 13.24 | 0.010508 | 0.01751%
| Controller to Battery | 4 | 8 | 0.0019967 | 48 | 16.55 | 0.033045 |  | 0.06884%
| Voltage Drop from Array to Controller ----->>>>>>> | [5 empty] | 0.2091 | 0.3485% | <<-- Keep Volt Drop under 3%
| Voltage drop from Array to Battery ---------->>>>>>> | [5 empty] | 0.24215 | 0.4174%
1 | You may make changes to any cell in Blue Text
2 | If you are testing Voltage drop for less than 8 Strings use String 1 then 2 etc..
3 | Can be used as a Single String Planing Tool by putting Zeros in Panel Amps for String 2 and String 8.
4 | Keep your voltage drop % as low as posable and as even as posable for each panel string.
5 | You may change the wire temp by using a (c) for Celsius or (f) for Fahrenheit in cell (B3). 50 deg. Celsius would be the standard.
6 | To use Wire Size 1/0, 2/0, 3/0, 4/0 you will need to use the Caps letter O not zero. 1/0=O 2/0=OO 3/0=OOO and so on.
7 | Max wire size is OOOO and Min wire size is 40 gage.
8 | You may want to use standard voltages like 24 volts from the panels and 12 volts at the batteries.
9 | When entering wire length use two way length. How long is each wire from the panel to the combiner box both ways? Same for all other wire runs.
Use at your own risk! Users accept responsibility for the use of these said calculations knowing there could be errors and should
be verified by other means. Creators of this Voltage Drop Calculator accepts Zero Responsibility for Good or Bad out come of it's use.

## Sheet2 (hidden)
AWG gauge | Diameter Inches | Diameter mm | Ohms per 1000 ft | Ohms per km | Maximum amps for chassis wiring | Maximum amps for power transmission
OOOO | 0.46 | 11.684 | 0.049 | 0.16072 | 380 | 302 | 4.9214e-05 | 21.1111
OOO | 0.4096 | 10.4038 | 0.0618 | 0.2027 | 328 | 239 | 6.207e-05
OO | 0.3648 | 9.2659 | 0.0779 | 0.25551 | 283 | 190 | 7.824e-05
O | 0.3249 | 8.2525 | 0.0983 | 0.32242 | 245 | 150 | 9.8729e-05
1 | 0.2893 | 7.3482 | 0.1239 | 0.40639 | 211 | 119 | 0.00012444
2 | 0.2576 | 6.543 | 0.1563 | 0.51266 | 181 | 94 | 0.00015698
3 | 0.2294 | 5.8268 | 0.197 | 0.64616 | 158 | 75 | 0.00019786
4 | 0.2043 | 5.1892 | 0.2485 | 0.81508 | 135 | 60 | 0.00024958
5 | 0.1819 | 4.6203 | 0.3133 | 1.0276 | 118 | 47 | 0.00031467
6 | 0.162 | 4.1148 | 0.3951 | 1.2959 | 101 | 37 | 0.00039682
7 | 0.1443 | 3.6652 | 0.4982 | 1.6341 | 89 | 30 | 0.00050038
8 | 0.1285 | 3.2639 | 0.6282 | 2.0605 | 73 | 24 | 0.00063094
9 | 0.1144 | 2.9058 | 0.7921 | 2.5981 | 64 | 19 | 0.00079556
10 | 0.1019 | 2.5883 | 0.9989 | 3.2764 | 55 | 15 | 0.0010033
11 | 0.0907 | 2.3038 | 1.26 | 4.1328 | 47 | 12 | 0.0012655
12 | 0.0808 | 2.0523 | 1.588 | 5.2086 | 41 | 9.3 | 0.0015949
13 | 0.072 | 1.8288 | 2.003 | 6.5698 | 35 | 7.4 | 0.0020117
14 | 0.0641 | 1.6281 | 2.525 | 8.282 | 32 | 5.9 | 0.002536
15 | 0.0571 | 1.4503 | 3.184 | 10.4435 | 28 | 4.7 | 0.0031979
16 | 0.0508 | 1.2903 | 4.016 | 13.1725 | 22 | 3.7 | 0.0040335
17 | 0.0453 | 1.1506 | 5.064 | 16.6099 | 19 | 2.9 | 0.0050861
18 | 0.0403 | 1.0236 | 6.385 | 20.9428 | 16 | 2.3 | 0.0064129
19 | 0.0359 | 0.91186 | 8.051 | 26.4073 | 14 | 1.8 | 0.0080861
20 | 0.032 | 0.8128 | 10.15 | 33.292 | 11 | 1.5 | 0.010194
21 | 0.0285 | 0.7239 | 12.8 | 41.984 | 9 | 1.2 | 0.012856
22 | 0.0254 | 0.64516 | 16.14 | 52.9392 | 7 | 0.92 | 0.01621
23 | 0.0226 | 0.57404 | 20.36 | 66.7808 | 4.7 | 0.729 | 0.020449
24 | 0.0201 | 0.51054 | 25.67 | 84.1976 | 3.5 | 0.577 | 0.025782
25 | 0.0179 | 0.45466 | 32.37 | 106.1736 | 2.7 | 0.457 | 0.032511
26 | 0.0159 | 0.40386 | 40.81 | 133.8568 | 2.2 | 0.361 | 0.040988
27 | 0.0142 | 0.36068 | 51.47 | 168.8216 | 1.7 | 0.288 | 0.051695
28 | 0.0126 | 0.32004 | 64.9 | 212.872 | 1.4 | 0.226 | 0.065183
29 | 0.0113 | 0.28702 | 81.83 | 268.4024 | 1.2 | 0.182 | 0.082187
30 | 0.01 | 0.254 | 103.2 | 338.496 | 0.86 | 0.142 | 0.10365
31 | 0.0089 | 0.22606 | 130.1 | 426.728 | 0.7 | 0.113 | 0.13067
32 | 0.008 | 0.2032 | 164.1 | 538.248 | 0.53 | 0.091 | 0.16482
2.0mm | 0.00787 | 0.2 | 169.39 | 555.61 | 0.51 | 0.088 | 0.17013
33 | 0.0071 | 0.18034 | 206.9 | 678.632 | 0.43 | 0.072 | 0.2078
1.8mm | 0.00709 | 0.18 | 207.5 | 680.55 | 0.43 | 0.072 | 0.20841
34 | 0.0063 | 0.16002 | 260.9 | 855.752 | 0.33 | 0.056 | 0.26204
1.6mm | 0.0063 | 0.16002 | 260.9 | 855.752 | 0.33 | 0.056 | 0.26204
35 | 0.0056 | 0.14224 | 329 | 1079.12 | 0.27 | 0.044 | 0.33044
1.4mm | 0.00551 | 0.14 | 339 | 1114 | 0.26 | 0.043 | 0.34048
36 | 0.005 | 0.127 | 414.8 | 1360 | 0.21 | 0.035 | 0.41661
1.25mm | 0.00492 | 0.125 | 428.2 | 1404 | 0.2 | 0.034 | 0.43007
37 | 0.0045 | 0.1143 | 523.1 | 1715 | 0.17 | 0.0289 | 0.52538
1.12mm | 0.00441 | 0.112 | 533.8 | 1750 | 0.163 | 0.0277 | 0.53613
38 | 0.004 | 0.1016 | 659.6 | 2163 | 0.13 | 0.0228 | 0.66248
1mm | 0.00394 | 0.1 | 670.2 | 2198 | 0.126 | 0.0225 | 0.67313
39 | 0.0035 | 0.0889 | 831.8 | 2728 | 0.11 | 0.0175 | 0.83543
40 | 0.0031 | 0.07874 | 1049 | 3440 | 0.09 | 0.0137 | 1.0536